## 046
| CAKRA MAKOTA SDN BHD | PURCHASE ORDER
NO. 138, TINGKAT 2, BLOK 4,
PUSAT PERNIAGAAN WORLDWIDE |  | DATE | 2026-07-13
JALAN KERATE 14/47, SEKSYEN 13, |  | PO # | CMSB/07/2026/M-0046
40675 SHAH ALAM, SELANGOR |  | TERM | 30 DAYS
VENDOR |  | DELIVER TO
TWO ADVANCED SDN BHD |  | CAKRA MAKOTA SDN BHD
27, JALAN 2, TAMAN GEMBIRA, |  | PEJABAT PENGURUSAN FASILITI
43500 SEMENYIH, |  | MENARA KERJA RAYA (BLOK G),
SELANGOR. |  | IBU PEJABAT JKR MALAYSIA,
JALAN SULTAN SALAHUDDIN,
62574 KUALA LUMPUR.
Email: |  | Email: | cakramakota.sb@gmail.com
Tel : | 012-3839073 | Tel: | 03-6209 4838
Attn : | MR/MRS YH WONG | Attn : | EN. MUHD NASRUL
STATIONERY
NO. | DESCRIPTION |  | QTY | UNIT PRICE (RM) | PRICE (RM)
DESCRIPTION :
1 | SPA 1020 |  | 6 | 15 | 90
2 | SPA 1115 |  | 8 | 16 | 128
3 | ABS 25MM ELBOW |  | 4 | 2.3 | 9.2
4 | ABS 25MM SOCKET |  | 4 | 1.9 | 7.6
5 | ABS 25MM VALVE SOCKET |  | 4 | 2.8 | 11.2
6 | ABS 25MM PT SOCKET |  | 4 | 5.5 | 22
7 | ABS 25MM END CAP |  | 4 | 1.9 | 7.6
8 | ABS 25MM PIPE (4 FEET) |  | 1 | 11 | 11
9 | ABS 32MM END CAP |  | 3 | 3.2 | 9.6
10 | ABS 32MM SOCKET |  | 2 | 3 | 6
11 | ABS 32MM ELBOW |  | 2 | 4 | 8
12 | ABS 32MM PIPE (5.8M) |  | 1 | 60 | 60
13 | OMRON MK2P-I 24VAC RELAY |  | 5 | 23.5 | 117.5
DISCOUNT |  |  |  |  | 487.7
Amount carried over to the next page (if any)
487.7
Comments or Special Instructions
Prepared By: |  | Verified By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :
Checked By : |  | Approved By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :

## 047
| CAKRA MAKOTA SDN BHD | PURCHASE ORDER
NO. 138, TINGKAT 2, BLOK 4,
PUSAT PERNIAGAAN WORLDWIDE |  | DATE | 2026-07-13
JALAN KERATE 14/47, SEKSYEN 13, |  | PO # | CMSB/07/2026/M-0047
40675 SHAH ALAM, SELANGOR |  | TERM | 30 DAYS
VENDOR |  | DELIVER TO
CARRIER (MALAYSIA) SDN BHD |  | CAKRA MAKOTA SDN BHD
NO. 10-F1, 10th FLOOR, TOWER 5@PFCC, |  | PEJABAT PENGURUSAN FASILITI
JALAN PUTERI 1/2, BANDAR PUTERI, |  | MENARA KERJA RAYA (BLOK G),
47100 PUCHONG, SELANGOR DARUL EHSAN |  | IBU PEJABAT JKR MALAYSIA,
JALAN SULTAN SALAHUDDIN,
62574 KUALA LUMPUR.
Email: |  | Email: | cakramakota.sb@gmail.com
Tel : | 013-3333147 | Tel: | 03-6209 4838
Attn : | MS PORKKODI A/P SUKAMARAN | Attn : | EN. MUHD NASRUL
MECHANICAL
NO. | DESCRIPTION |  | QTY | UNIT PRICE (RM) | PRICE (RM)
DESCRIPTION :
CARRIER 19XR Series CH 3
Model: 19XR Frame 4 S/N: XR4L4138
A | Supply labour, tools and material to perform repair work as per below scope of works:
1.00 | Materials required for repair work for CH3:
1.01 | Recovery cylinder rental (60kg) |  | 12 cyls | 250 | 3000
1.02 | Nitrogen |  | 1 Lot | 1000 | 1000
1.03 | O-ring |  | 2 pc | 30 | 60
1.04 | ICVC board |  | 1 pc | 17000 | 17000
1.05 | Guide vane actuator motor |  | 1 pc | 28000 | 28000
1.06 | Chain and sprocket assembly |  | 1 set | 5000 | 5000
1.07 | Temperature sensor |  | 4 pc | 800 | 3200
1.08 | Diffuser actuator motor |  | 1 pc | 30000 | 30000
1.09 | ISM board |  | 1 pc | 23000 | 23000
1.10 | Refrigerant - 60kg cylinder |  | 3 cyls | 3000 | 9000
1.11 | Soft starter |  | 1 pc | 55000 | 55000
Below are the tools and labours to perform the schedule repair works
1.12 | To pump out refrigerant into recovery empty cylinders |  | 1 Lot | 43600 | 43600
1.13 | To pressurize system with nitrogen and check leak
1.14 | To vacuum system
1.15 | To charge-in back refrigerant into system
1.16 | Top-up refrigerant if there is any refrigerant loss
1.17 | Calibration of chiller transducer
1.18 | Replace oil pump and bearing terminal O-ring
1.19 | To supply and replace diffuser actuator motor
1.20 | Replace guide vane actuator motor
1.21 | Replace set of chain and sprocket
1.22 | Replace chilled & condenser water temperature sensors
1.23 | To replace ICVC board c/w setting configuration work
1.24 | To install new soft starter for chiller incoming power supply
1.25 | To carry out existing chiller insulation replacement work
1.26 | Transportation and mobilization of manpower
1.27 | Testing and re-commissioning of chiller
| A:Total price without SST |  |  |  | 217860
| A:SST 8% for labour only |  |  |  | 3488
| A: Total price with SST |  |  |  | 221348
Supply labour, tools and materiasl to perform annual oil change as per below scope of works:
B
2 | Materials required for annual shutdown for CH3
2.01 | Oil filter |  | 1 pc | 3300 | 3300
2.02 | Oil strainer |  | 1 pc | 700 | 700
2.03 | Compressor oil (18L) |  | 2 drum | 5500 | 11000
2.04 | Compressor oil (4L) |  | 2 drum | 3500 | 7000
2.05 | Nylon brush |  | 3 pc | 180 | 540
2.06 | Filter drier core 5/8' |  | 1 pc | 580 | 580
2.07 | Filter drier core 3/8'' |  | 1 pc | 580 | 580
2.08 | Nitrogen |  | 1 Lot | 1000 | 1000
Below are the tools and labours to perform annual shutdown works:
1.12 | To pump down refrigerant into condenser vessel |  | 1 Lot | 5300 | 5300
1.13 | To drain out and contain used compressor oil
1.14 | To replace filters and filter drier
1.15 | To perform condenser tubes cleaning by opening one side of the condenser vessel end cover
1.16 | To pressurize system using nitrogen and check for leaks
1.17 | To vacuum system and charge in new compressor oil
1.18 | To recalibrate all temperature sensors and pressure transducers
1.19 | Testing and recommissioning of chiller
| B:Total price without SST |  |  |  | 30000
| B:SST 8% for labour only |  |  |  | 424
| B: Total price with SST |  |  |  | 30424
C | Supply labour, tools and materials to perform compressor overhaul as per below scope of works:
3.00 | Materials required for compressor overhaul for CH3
3.01 | High speed roller bearing |  | 1 pc | 12900 | 12900
3.02 | Low speed bearing |  | 2 pc | 30500 | 61000
3.03 | Inner diffuser |  | 1 pc | 88000 | 88000
3.04 | Inner ring shaft roller |  | 3 pcs | 3500 | 3500
3.05 | Roller |  | 3 pcs | 4800 | 4800
3.06 | Shaft bearing |  | 1 pc | 5300 | 5300
3.07 | Impeller shim |  | 1 pc | 4800 | 4800
3.08 | O-ring and gasket |  | 1 set | 10000 | 10000
3.09 | Transducer & transducer cable |  | 1 pc | 1200 | 1200
3.10 | Bearing temperature sensor |  | 1 pc | 1050 | 1050
3.11 | service and revarnish motor stator coil & rotor balancing |  | 1 Lot | 18000 | 18000
Below are the tools and labours to perform compressor overhaul works:
3.12 | Dismantle float chamber and service |  | 1 Lot | 30490 | 30490
3.13 | Replace bearings, inner diffuser, ring shaft roller, shim
3.14 | Replace bearing temperature sensor, impeller
3.15 | Supply and replace O-ring and gaskets
3.16 | To reassemble compressor
3.17 | Oil pump service
3.18 | Supply and replace transducer and transducer cable
3.19 | Pressurize the system with nitrogen and carry out leak
3.20 | Testing and commissioning
| C:Total price without SST |  |  |  | 257640
| C:SST 8% labour only |  |  |  | 2439.2
| C: Total price with SST |  |  |  | 260079.2
| (A+B+C) Total price without SST |  |  |  | 505500
| Special discount on parts (3%) |  |  |  | 15165
| (A+B+C) Total price after discount |  |  |  | 490335
| (A+B+C) SST 8% |  |  |  | 6351.2
| (A+B+C) Total price with SST |  |  |  | 496686.2
Amount carried over to the next page (if any)
496686.2
Comments or Special Instructions
Term Payment : Deed Of Assignment
(Security for direct payments from a third party)
Prepared By: |  | Verified By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :
Checked By : |  | Approved By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :

## 051
| CAKRA MAKOTA SDN BHD | PURCHASE ORDER
NO. 138, TINGKAT 2, BLOK 4,
PUSAT PERNIAGAAN WORLDWIDE |  | DATE | 2026-07-22
JALAN KERATE 14/47, SEKSYEN 13, |  | PO # | CMSB/2026/PO-0053
40675 SHAH ALAM, SELANGOR |  | TERM | 30 DAYS
VENDOR |  | DELIVER TO
CARRIER (MALAYSIA) SDN BHD |  | CAKRA MAKOTA SDN BHD
NO. 10-F1, 10th FLOOR, TOWER 5@PFCC, |  | PEJABAT PENGURUSAN FASILITI
JALAN PUTERI 1/2, BANDAR PUTERI, |  | MENARA KERJA RAYA (BLOK G),
47100 PUCHONG, SELANGOR DARUL EHSAN |  | IBU PEJABAT JKR MALAYSIA,
JALAN SULTAN SALAHUDDIN,
62574 KUALA LUMPUR.
Email: |  | Email: | cakramakota.sb@gmail.com
Tel : | 013-3333147 | Tel: | 03-6209 4838
Attn : | MS PORKKODI A/P SUKAMARAN | Attn : | EN. MUHD NASRUL
MECHANICAL
NO. | DESCRIPTION |  | QTY | UNIT PRICE (RM) | PRICE (RM)
DESCRIPTION :
CARRIER 19XR SerCARRIER 19XR- Series Chiller 2ies CH 3
A | Material needed for repair work
1.01 | Diffuser actuator motor |  | 1 pc | 30000
B | Below are the tools and labours to perform the schedule repair works: |  | 1 Lot | 1000 | 1000
1.02 | To supply and replace diffuser actuator motor |  | 2 pc | 30 | 60
1.03 | Transportation and mobilization of manpower |  | 1 pc | 17000 | 17000
1.04 | Testing and re-commissioning of chiller |  | 1 pc | 28000 | 28000
| C:Total price without SST |  |  |  | 34000
| C:SST 8% labour only |  |  |  | 320
Amount carried over to the next page (if any)
34320
Comments or Special Instructions
Term Payment : Deed Of Assignment
(Security for direct payments from a third party)
Prepared By: |  | Verified By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :
Checked By : |  | Approved By :
…………....…………….……………………… |  | ……….…..……………………………..
Date: |  | Date :